## ISITMA YUK TABLOSU
ISITMA YUK TABLOSU | [6 empty] | ISITMA YUK TABLOSU
Kcal/h | [6 empty] | kW
ÇAP | ∆T=1 °C |  | ∆T=10 °C |  | ∆T=20 °C |  | ÇAP | ∆T=1 °C |  | ∆T=10 °C |  | ∆T=15 °C |  | ∆T=20 °C |  | HIZ(m/sn)
1/2" | - | 180 | - | 1800 | - | 3600 | 1/2" | - | 0.2093 | - | 2.093 | - | 3.1395 | - | 4.186 | 0.28215
3/4" | 180 | 410 | 1800 | 4100 | 3600 | 8200 | 3/4" | 0.2093 | 0.47674 | 2.093 | 4.7674 | 3.1395 | 7.1512 | 4.186 | 9.5349 | 0.3615
1" | 410 | 850 | 4100 | 8500 | 8200 | 17000 | 1" | 0.47674 | 0.98837 | 4.7674 | 9.8837 | 7.1512 | 14.8256 | 9.5349 | 19.7674 | 0.47965
11/4" | 850 | 1895 | 8500 | 18950 | 17000 | 37900 | 11/4" | 0.98837 | 2.2035 | 9.8837 | 22.0349 | 14.8256 | 33.0523 | 19.7674 | 44.0698 | 0.65267
11/2" | 1895 | 2800 | 18950 | 28000 | 37900 | 56000 | 11/2" | 2.2035 | 3.2558 | 22.0349 | 32.5581 | 33.0523 | 48.8372 | 44.0698 | 65.1163 | 0.61719
2" | 2800 | 5050 | 28000 | 50500 | 56000 | 101000 | 2" | 3.2558 | 5.8721 | 32.5581 | 58.7209 | 48.8372 | 88.0814 | 65.1163 | 117.4419 | 0.71242
21/2" | 5050 | 11350 | 50500 | 113500 | 101000 | 227000 | 21/2" | 5.8721 | 13.1977 | 58.7209 | 131.9767 | 88.0814 | 197.9651 | 117.4419 | 263.9535 | 0.94744
3" | 11350 | 17550 | 113500 | 175500 | 227000 | 351000 | 3" | 13.1977 | 20.407 | 131.9767 | 204.0698 | 197.9651 | 306.1047 | 263.9535 | 408.1395 | 0.96712
4" | 17550 | 29700 | 175500 | 297000 | 351000 | 594000 | 4" | 20.407 | 34.5349 | 204.0698 | 345.3488 | 306.1047 | 518.0233 | 408.1395 | 690.6977 | 1.0475
5" | 29700 | 52500 | 297000 | 525000 | 594000 | 1050000 | 5" | 34.5349 | 61.0465 | 345.3488 | 610.4651 | 518.0233 | 915.6977 | 690.6977 | 1220.9302 | 1.185
6" | 52500 | 85000 | 525000 | 850000 | 1050000 | 1700000 | 6" | 61.0465 | 98.8372 | 610.4651 | 988.3721 | 915.6977 | 1482.5581 | 1220.9302 | 1976.7442 | 1.3324
8" | 85000 | 189500 | 850000 | 1895000 | 1700000 | 3790000 | 8" | 98.8372 | 220.3488 | 988.3721 | 2203.4884 | 1482.5581 | 3305.2326 | 1976.7442 | 4406.9767 | 1.6708
10" | 189500 | 350000 | 1895000 | 3500000 | 3790000 | 7000000 | 10" | 220.3488 | 406.9767 | 2203.4884 | 4069.7674 | 3305.2326 | 6104.6512 | 4406.9767 | 8139.5349 | 1.975
NOT | [6 empty] | NOT
FARKLI ΔT İÇİN | [6 empty] | FARKLI ΔT İÇİN
ISITMA YUKU=ΔT* ( 1 °C SUTUNUNDAKİ DEĞER) FORMULU KULLANILIR | [6 empty] | ISITMA YUKU=ΔT* ( 1 °C SUTUNUNDAKİ DEĞER) FORMULU KULLANILIR
1/2" | 3200 | 160
3/4" | 8000 | 400
1" | 18000 | 900
11/4" | 37900 | 1895
11/2" | 56000 | 2800
2" | 101000 | 5050
21/2" | 227000 | 11350
3" | 351000 | 17550
4" | 594000 | 29700
5" | 1050000 | 52500
6" | 1700000 | 85000
8" | 3790000 | 189500
10" | 8710000 | 435500

## SOGUTMA YUK TABLOSU
SOĞUTMA YÜK TABLOSU | [5 empty] | SOĞUTMA YÜK TABLOSU
Kcal/h | [5 empty] | kW
ÇAP | ∆T=1 °C |  | ∆T=5 °C |  |  | ÇAP | ∆T=1 °C |  | ∆T=5 °C |  | HIZ(m/sn)
3/4" | - | 500 | - | 2500 |  | 3/4" | - | 0.5814 | - | 2.907 | 0.44085
1" | 500 | 1040 | 2500 | 5200 |  | 1" | 0.5814 | 1.2093 | 2.907 | 6.0465 | 0.58686
11/4" | 1040 | 2200 | 5200 | 11000 |  | 11/4" | 1.2093 | 2.7 | 6.0465 | 13.5 | 0.75771
11/2" | 2200 | 3300 | 11000 | 16500 |  | 11/2" | 2.7 | 3.8372 | 13.5 | 19.186 | 0.72741
2" | 3300 | 5800 | 16500 | 29000 |  | 2" | 3.8372 | 6.7442 | 19.186 | 33.7209 | 0.81822
21/2" | 5800 | 11600 | 29000 | 58000 |  | 21/2" | 6.7442 | 13.4884 | 33.7209 | 67.4419 | 0.96831
3" | 11600 | 20000 | 58000 | 100000 |  | 3" | 13.4884 | 23.2558 | 67.4419 | 116.2791 | 1.1021
4" | 20000 | 32800 | 100000 | 164000 |  | 4" | 23.2558 | 38.1395 | 116.2791 | 190.6977 | 1.1568
5" | 32800 | 60000 | 164000 | 300000 |  | 5" | 38.1395 | 69.7674 | 190.6977 | 348.8372 | 1.3543
6" | 60000 | 96000 | 300000 | 480000 |  | 6" | 69.7674 | 111.6279 | 348.8372 | 558.1395 | 1.5048
8" | 96000 | 220000 | 480000 | 1100000 |  | 8" | 111.6279 | 255.814 | 558.1395 | 1279.0698 | 1.9397
NOT
[5 empty] | 1 | FARKLI ΔT İÇİN
SOĞUTMA YUKU=ΔT* ( 1 °C SUTUNUNDAKİ DEĞER) FORMULU KULLANILIR

## HIZ KONTROL
[10 empty] | ISITMA SİSTEMİ | [9 empty] | SOĞUTMA SİSTEMİ
7410-+
CAPACITY(Kw) | CAPACITY | TEMPERATURE DIFFERENCE | C | DENSITY | FLOW RATE | FLOW RATE | FLOW RATE | PIPE DIAMETER | VELOCİTY | CAPACITY | CAPACITY | TEMPERATURE DIFFERENCE | C | DENSITY | FLOW RATE | FLOW RATE | FLOW RATE | PIPE DIAMETER | VELOCİTY | CAPACITY | CAPACITY | TEMPERATURE DIFFERENCE | C | DENSITY | FLOW RATE | FLOW RATE | FLOW RATE | PIPE DIAMETER | VELOCİTY
Kcal/h | Kw | °C | Kj/Kg °C | Kg/lt | lt/s | L/h | m³/s | mm | m/s | Kcal/h | Kw | °C | Kj/Kg °C | Kg/lt | lt/s | L/h | m³/s | mm | m/s | Kcal/h | Kw | °C | Kj/Kg °C | Kg/lt | lt/s | L/h | m³/s | mm | m/s
180 | 0.2093 | 1 | 4.2 | 1 | 0.049834 | 179.402 | 4.9834e-05 | 15 | 0.28215 | 180 | 0.2093 | 1 | 4.2 | 1 | 0.049834 | 179.402 | 4.9834e-05 | 15 | 0.28215 | 500 | 0.5814 | 1 | 4.2 | 1 | 0.13843 | 498.3389 | 0.00013843 | 20 | 0.44085
410 | 0.47674 | 1 | 4.2 | 1 | 0.11351 | 408.6379 | 0.00011351 | 20 | 0.3615 | 410 | 0.47674 | 1 | 4.2 | 1 | 0.11351 | 408.6379 | 0.00011351 | 20 | 0.3615 | 1040 | 1.2093 | 1 | 4.2 | 1 | 0.28793 | 1036.5449 | 0.00028793 | 25 | 0.58686
850 | 0.98837 | 1 | 4.2 | 1 | 0.23533 | 847.1761 | 0.00023533 | 25 | 0.47965 | 850 | 0.98837 | 1 | 4.2 | 1 | 0.23533 | 847.1761 | 0.00023533 | 25 | 0.47965 | 2200 | 2.5581 | 1 | 4.2 | 1 | 0.60908 | 2192.691 | 0.00060908 | 32 | 0.75771
1895 | 2.2035 | 1 | 4.2 | 1 | 0.52464 | 1888.7043 | 0.00052464 | 32 | 0.65267 | 1895 | 2.2035 | 1 | 4.2 | 1 | 0.52464 | 1888.7043 | 0.00052464 | 32 | 0.65267 | 3300 | 3.8372 | 1 | 4.2 | 1 | 0.91362 | 3289.0365 | 0.00091362 | 40 | 0.72741
2800 | 3.2558 | 1 | 4.2 | 1 | 0.77519 | 2790.6977 | 0.00077519 | 40 | 0.61719 | 2800 | 3.2558 | 1 | 4.2 | 1 | 0.77519 | 2790.6977 | 0.00077519 | 40 | 0.61719 | 5800 | 6.7442 | 1 | 4.2 | 1 | 1.6058 | 5780.7309 | 0.0016058 | 50 | 0.81822
5050 | 5.8721 | 1 | 4.2 | 1 | 1.3981 | 5033.2226 | 0.0013981 | 50 | 0.71242 | 5050 | 5.8721 | 1 | 4.2 | 1 | 1.3981 | 5033.2226 | 0.0013981 | 50 | 0.71242 | 11600 | 13.4884 | 1 | 4.2 | 1 | 3.2115 | 11561.4618 | 0.0032115 | 65 | 0.96831
11350 | 13.1977 | 1 | 4.2 | 1 | 3.1423 | 11312.2924 | 0.0031423 | 65 | 0.94744 | 11350 | 13.1977 | 1 | 4.2 | 1 | 3.1423 | 11312.2924 | 0.0031423 | 65 | 0.94744 | 20000 | 23.2558 | 1 | 4.2 | 1 | 5.5371 | 19933.5548 | 0.0055371 | 80 | 1.1021
17550 | 20.407 | 1 | 4.2 | 1 | 4.8588 | 17491.6944 | 0.0048588 | 80 | 0.96712 | 17550 | 20.407 | 1 | 4.2 | 1 | 4.8588 | 17491.6944 | 0.0048588 | 80 | 0.96712 | 32800 | 38.1395 | 1 | 4.2 | 1 | 9.0808 | 32691.0299 | 0.0090808 | 100 | 1.1568
29700 | 34.5349 | 1 | 4.2 | 1 | 8.2226 | 29601.3289 | 0.0082226 | 100 | 1.0475 | 29700 | 34.5349 | 1 | 4.2 | 1 | 8.2226 | 29601.3289 | 0.0082226 | 100 | 1.0475 | 60000 | 69.7674 | 1 | 4.2 | 1 | 16.6113 | 59800.6645 | 0.016611 | 125 | 1.3543
52500 | 61.0465 | 1 | 4.2 | 1 | 14.5349 | 52325.5814 | 0.014535 | 125 | 1.185 | 52500 | 61.0465 | 1 | 4.2 | 1 | 14.5349 | 52325.5814 | 0.014535 | 125 | 1.185 | 96000 | 111.6279 | 1 | 4.2 | 1 | 26.5781 | 95681.0631 | 0.026578 | 150 | 1.5048
84280 | 98 | 1 | 4.2 | 1 | 23.3333 | 84000 | 0.023333 | 150 | 1.3211 | 85000 | 98.8372 | 1 | 4.2 | 1 | 23.5327 | 84717.608 | 0.023533 | 150 | 1.3324 | 220000 | 255.814 | 1 | 4.2 | 1 | 60.9081 | 219269.103 | 0.060908 | 200 | 1.9397
| 220 | 1 | 4.2 | 1 | 52.381 | 188571.4286 | 0.052381 | 200 | 1.6682 | 189500 | 220.3488 | 1 | 4.2 | 1 | 52.464 | 188870.4319 | 0.052464 | 200 | 1.6708 | 350000 | 406.9767 | 1 | 4.2 | 1 | 96.8992 | 348837.2093 | 0.096899 | 250 | 1.975
| 407 | 1 | 4.2 | 1 | 96.9048 | 348857.1429 | 0.096905 | 250 | 1.9751 | 350000 | 406.9767 | 1 | 4.2 | 1 | 96.8992 | 348837.2093 | 0.096899 | 250 | 1.975
|  |  |  | 180 | 0.2093
|  |  |  | 410 | 0.47674
|  |  |  | 850 | 0.98837
|  |  |  | 1895 | 2.2035
|  |  |  | 2800 | 3.2558 | [14 empty] | 500
|  |  |  | 5050 | 5.8721 | [14 empty] | 1040
|  |  |  | 11350 | 13.1977 | [14 empty] | 2200
|  |  |  | 17550 | 20.407 | [14 empty] | 3300
|  |  |  | 29700 | 34.5349 | [14 empty] | 5800
|  |  |  | 52500 | 61.0465 | [14 empty] | 11600
|  |  |  | 85000 | 98.8372 | [14 empty] | 20000
|  |  |  | 189500 | 220.3488 | [14 empty] | 32800
|  |  |  | 350000 | 406.9767 | [14 empty] | 60000
96000
220000
SOĞUTMA SİSTEMİ
[10 empty] | CAPACITY | CAPACITY | TEMPERATURE DIFFERENCE | C | DENSITY | FLOW RATE | FLOW RATE | FLOW RATE | PIPE DIAMETER | VELOCİTY
[10 empty] | Kcal/h | Kw | °C | Kj/Kg °C | Kg/lt | lt/s | L/h | m³/s | mm | m/s
[10 empty] | 500 | 0.5814 | 1 | 4.2 | 1 | 0.13843 | 498.3389 | 0.00013843 | 20 | 0.44085
[10 empty] | 1040 | 1.2093 | 1 | 4.2 | 1 | 0.28793 | 1036.5449 | 0.00028793 | 25 | 0.58686
[10 empty] | 2200 | 2.5581 | 1 | 4.2 | 1 | 0.60908 | 2192.691 | 0.00060908 | 32 | 0.75771
[10 empty] | 3300 | 3.8372 | 1 | 4.2 | 1 | 0.91362 | 3289.0365 | 0.00091362 | 40 | 0.72741
[10 empty] | 5800 | 6.7442 | 1 | 4.2 | 1 | 1.6058 | 5780.7309 | 0.0016058 | 50 | 0.81822
[10 empty] | 11600 | 13.4884 | 1 | 4.2 | 1 | 3.2115 | 11561.4618 | 0.0032115 | 65 | 0.96831
[10 empty] | 20000 | 23.2558 | 1 | 4.2 | 1 | 5.5371 | 19933.5548 | 0.0055371 | 80 | 1.1021
[10 empty] | 32800 | 38.1395 | 1 | 4.2 | 1 | 9.0808 | 32691.0299 | 0.0090808 | 100 | 1.1568
[10 empty] | 60000 | 69.7674 | 1 | 4.2 | 1 | 16.6113 | 59800.6645 | 0.016611 | 125 | 1.3543
[10 empty] | 96000 | 111.6279 | 1 | 4.2 | 1 | 26.5781 | 95681.0631 | 0.026578 | 150 | 1.5048
[10 empty] | 220000 | 255.814 | 1 | 4.2 | 1 | 60.9081 | 219269.103 | 0.060908 | 200 | 1.9397
[10 empty] | CAPACITY | CAPACITY | TEMPERATURE DIFFERENCE | C | DENSITY | FLOW RATE | FLOW RATE | FLOW RATE | PIPE DIAMETER | VELOCİTY
[10 empty] | Kcal/h | Kw | °C | Kj/Kg °C | Kg/lt | lt/s | L/h | m³/s | mm | m/s
[10 empty] | 2500 | 2.907 | 5 | 4.2 | 1 | 0.13843 | 498.3389 | 0.00013843 | 20 | 0.44085
[10 empty] | 5200 | 6.0465 | 5 | 4.2 | 1 | 0.28793 | 1036.5449 | 0.00028793 | 25 | 0.58686 | 500
[10 empty] | 11000 | 12.7907 | 5 | 4.2 | 1 | 0.60908 | 2192.691 | 0.00060908 | 32 | 0.75771 | 1040
[10 empty] | 16500 | 19.186 | 5 | 4.2 | 1 | 0.91362 | 3289.0365 | 0.00091362 | 40 | 0.72741 | 2200
[10 empty] | 29000 | 33.7209 | 5 | 4.2 | 1 | 1.6058 | 5780.7309 | 0.0016058 | 50 | 0.81822 | 3300
[10 empty] | 58000 | 67.4419 | 5 | 4.2 | 1 | 3.2115 | 11561.4618 | 0.0032115 | 65 | 0.96831 | 5800
[10 empty] | 100000 | 116.2791 | 5 | 4.2 | 1 | 5.5371 | 19933.5548 | 0.0055371 | 80 | 1.1021 | 11600
[10 empty] | 164000 | 190.6977 | 5 | 4.2 | 1 | 9.0808 | 32691.0299 | 0.0090808 | 100 | 1.1568 | 20000
[10 empty] | 300000 | 348.8372 | 5 | 4.2 | 1 | 16.6113 | 59800.6645 | 0.016611 | 125 | 1.3543 | 32800
[10 empty] | 480000 | 558.1395 | 5 | 4.2 | 1 | 26.5781 | 95681.0631 | 0.026578 | 150 | 1.5048 | 60000
[10 empty] | 1100000 | 1279.0698 | 5 | 4.2 | 1 | 60.9081 | 219269.103 | 0.060908 | 200 | 1.9397 | 96000
220000